ANHUI JIEZOU NEW ENERGY CO.,LTD.

| Product Certification |  |  |
| --- | --- | --- |
| Product Name: Three Phase Pad Mounted Transformer Model: ZGS-H-225/24940-480/277 Factory Serial: JM2307043 |  |  |
| Test result: This transformer has been tested to meet the requirements of IEEE standard, test Qualified and allowed to leave the factory. |  |  |
| Inspectors: ZHANG YAOFENG |  |  |
| Date： | Sep.20 2023 |  |

ADD: FengYang Economic Development Zone,FengYang County,Anhui Province Chin

| 1 、Specification |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Rated Capacity （KVA） | 225 | Product Type |  |  | ZGS-H-225 |  |  |  | 60HZ |  | Factory Serial No. |  | JM2307043 |  |  |
| 3Voltage Combination | HV(kV) | 24.94 |  |  | Current |  |  | HV (A) | 5.209 |  | Angular displacement |  | YNyn0 |  |  |
|  | LV(kV) | 0.6 |  |  |  |  |  | LV( A) | 216.5 |  |  |  |  |  |  |
| 2 、 Measurement of voltage ratio |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Tapping Position | HV and LVThe Voltage Value of the Test The Grade and Accuracy:QJ3 5A Grade 0.2 | HV（V） |  |  | LV（V） |  |  |  | HV/LV（%） |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | AB/ab |  |  | BC/bc |  |  | AC/ca |
| 1 |  | 26187 |  |  | 600 |  |  |  | 0.06 |  |  | 0.08 |  |  | 0.05 |
| 2 |  | 25563.5 |  |  |  |  |  |  | 0.10 |  |  | 0.12 |  |  | 0.09 |
| 3 |  | 24940 |  |  |  |  |  |  | 0.14 |  |  | 0.16 |  |  | 0.13 |
| 4 |  | 24316.5 |  |  |  |  |  |  | 0.12 |  |  | 0.14 |  |  | 0.11 |
| 5 |  | 23693 |  |  |  |  |  |  | 0.10 |  |  | 0.13 |  |  | 0.09 |
| 3 、 Measurement of winding resistance （Routine） |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Tapping Position | Winding Resistance Measurement | HV (Ω) |  |  |  |  |  |  |  |  |  |  |  | LV(Ω) |  |
|  |  | H0H1A | H0H2A |  |  | H0H3A |  |  | H1AH1B | H2AH2B |  | H3AH3B |  | xox1 | 0.006986 |
| 1 |  | 18.07 | 17.94 |  |  | 18.01 |  |  | 36.01 | 35.95 |  | 36.08 |  | xox2 | 0.006909 |
| 2 |  | 17.60 | 17.47 |  |  | 17.53 |  |  | 35.07 | 35.00 |  | 35.14 |  | xox3 | 0.006798 |
| 3 |  | 17.13 | 17.00 |  |  | 17.06 |  |  | 34.12 | 34.06 |  | 34.19 |  | x1x2 | 0.01364 |
| 4 |  | 16.66 | 16.52 |  |  | 16.58 |  |  | 33.18 | 33.12 |  | 33.24 |  | x2x3 | 0.01347 |
| 5 |  | 16.17 | 16.04 |  |  | 16.10 |  |  | 32.21 | 32.13 |  | 32.27 |  | x3x1 | 0.01355 |
| The Meter NO. and Grade of Accuracy |  | HCR3102A Grade 0.2 |  | Temperature |  |  |  |  | 28 ℃ |  | Humidity |  |  | 100% |  |
| 4 、No-load loss and no-load current test. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test Items |  | No-Load Loss at 100% rated voltage W |  |  |  |  |  |  |  | No-Load Current % |  |  |  |  |  |
| Measured Value |  | 479 |  |  |  |  |  |  |  | 0.32 |  |  |  |  |  |
| 5 、Load loss and Short circuit test. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test Items | Load Loss at 85°C and rated voltage W |  |  |  |  |  | Total Loss W |  |  | Short Circuit Impedance at 85°C |  |  |  |  |  |
| Measured Value | 2940 |  |  |  |  |  | 3419 |  |  | 4.40 |  |  |  |  |  |

| 6 、 Applied voltage test |  |  |  |  |
| --- | --- | --- | --- | --- |
| Power Frequency withstand Voltage Test |  |  |  |  |
| Test Time | 60 S |  |  |  |
| The Test Voltage(kV) | HV 40 /LV10 |  |  |  |
| 7 、Induced Over Voltage Withstand Test |  |  |  |  |
| Induced Over Voltage Withstand Test(kV) | 1.2 (rms) for L.V. bushing |  |  |  |
| 8 、 Insulation Resistance test |  |  |  |  |
| location | Insulation Resistance( M Ω) at 28℃ R60 |  |  |  |
| HV-LV | >2500 |  |  |  |
| HV-E | >2500 |  |  |  |
| LV-E | >2500 |  |  |  |
| 9 、 Other Information. |  |  |  |  |
| The Active Part’s Weight of Lifting | The Weight of Insulation Oil | Total Weight | The Temperature Rise of the Oil | Oil Pressure |
| 888kg | 1000kg | 2510kg | ＜65K | 45KV |
| 10 、Leakage test （Routine） |  |  |  |  |
| Test method | Applied pressure（kPa） | Duration（h） | Residual pressure（kPa） | Result |
| The static pressure method | 20 | 12 | 18 | No leakage and no damage |
| 11、 Outer inspection |  |  |  |  |
| The nameplate, sign, earthing terminal, mark of terminal meets the requirement. There is no evidence of leakage. |  |  |  |  |
| Test Date: 20-9-2023 |  |  |  |  |