## 300kva 4.16KV
300 kVA,Primary 7200 Delta Secondary 600 Delta
预付时间 |  | 2024-05-27
外形图提交时间 |  | 预付后1-2周
生产时间要求 |  | 外形图确认后10周
描述 |  | 提供内容
标准和使用国家 |  | CSA C227.4,CSA802.1 加拿大
Type |  | Radial feed pad mount
Installation |  | Outdoor
Altitude above sea level/Ambient temperature | m/℃ | 1000/50
Altitude |  | ≤1500m
Rated Power | kVA | 300
HV | V | 7200 Delta
LV | V | 600
Rated Frequency | Hz | 60
Cooling System |  | ONAN
Number of winding |  | 2
Number of phase |  | 3
Core/Shell |  | Core type
Refrigerant |  | Mineral oil type II (PCB FREE)
Working-Temperature | °C | -40°C to +40°C
Cooling Method |  | ONAN
The temperature rise -Top oil | °C | 65
The temperature rise --Winding | °C | 65
Hot spot | °C | 80
Losses
No load losses at rated voltage and rated frequency on principal tap | W | 根据标准
Load loss at rated voltage | W | 根据标准
Tolerance |  | 根据标准
Vector Group |  | 根据标准
Core material |  | Grain oriented silicon steel
Core legged |  | 3
Winding material |  | 铝
Tap changer
On load or off-circuit |  | off-circuit
Position of tapped winding |  | HV
Tap Voltages HV | % | ±2x2.5%
High voltage electrical characteristics of transformers and assembled load break terminals
Insulation class | kV | 根据标准
BIL | kV | 根据标准
Low voltage
Insulation class | kV | 1.2
BIL | kV | 30
Audible sound level | db | 根据标准
Short-circuit capability
Impedance | % | 3.78 – 4.6%
Impedance tolerance |  | ±7.5%
Tank |  | Mild steel
Colors |  | Munsell Green
Total Dimentions
Height 高 | mm | 根据标准
Depth 深 | mm | 根据标准
Width 宽 | mm | 根据标准
Weight 重量
Oil 油 | kg | 根据标准
Total 总重 | kg | 根据标准
Accessories including: 配件
Lifting lug 吊耳 |  | 有，根据标准
Hinged door 铰链门 |  | 有，根据标准
Parking stand bracket 挂架 |  | 有，根据标准
LV bushing 低压套管 |  | 有，根据标准
Pressure relief valve 压力释放阀 |  | 有，根据标准
Drain Valve 放油阀 |  | 有，根据标准
Ground Strap copper 接地铜条 |  | 有，根据标准
HV bushing insert 高压套管负载插头 |  | 有，根据标准
Ground pads 接地铜板 |  | 有，根据标准
Nameplate 铭牌 |  | 有，根据标准
Bayonet fuse 插入式熔丝 |  | 有，根据标准
Tap changer 调压开关 |  | 有，根据标准
LB switch 负荷开关 |  | 有，根据标准
Thermometer 油温计 |  | 有，根据标准
Oil level gauge 油位计 |  | 有，根据标准
Pressure vacuum gauge 压力真空表 |  | 有，根据标准
Bushing well 套管座 |  | 有，根据标准
Door handle 门把手 |  | 有，根据标准
其他要求： | 其他未要求细节，都可按加标标准要求设计