## sheet1
NO. | 产品描述-英文 | 产品描述-中文 | 参数值 | 数量 | 单价
| Power Transformer Capacity: 10 MVA Cooling Method: ONAN Frequency: 60 Hz High Voltage (Primary Side, HV): 25 kV, BIL 150 kV Low Voltage (Secondary Side, LV): 13.2 / 7.62 kV, BIL 95 kV Vector Group: Dyn1 Impedance: 7% at 10 MVA base value (tolerance ±10%) Tap Changer: No-load tap changer, range ±5% (2.5% steps) Temperature Rise: 65°C base temperature rise Oil: Mineral oil Windings: Copper Bushings: High-voltage side mounted on top; low-voltage and neutral sides mounted in NEMA 4 junction boxes Surge Arresters: High-voltage side equipped with substation-grade polymer surge arresters, MCOV rated at 15.3 kV Online Monitoring: Each transformer is equipped with a simplified online dissolved gas analysis monitoring system that monitors hydrogen, at a minimum Temperature Monitor: Qualitrol Model ITM 509 transformer temperature monitor with a life-discharge option Relays: Includes gas relays (ABB Model 12 or equivalent), surge pressure relays (Qualitrol Model 900), etc. Seismic Rating: LOW (must comply with IEEE 693 Annex U) CSA certification required | 主变 容量：10 MVA 冷却方式：ONAN 频率：60 Hz 高压（一次侧 HV）：25 kV，BIL 150 kV 低压（二次侧 LV）：13.2 / 7.62 kV，BIL 95 kV 联结组别：Dyn1 阻抗：在10MVA基值下为 7%（允许偏差 ±10%） 分接开关：无励磁分接开关，范围 ±5%（步长2.5%） 温升：65°C 基础温升 油：矿物油 绕组：铜 套管：高压侧顶部安装；低压侧和中性点侧面安装在NEMA 4接线盒内 避雷器：高压侧配备站级聚合物避雷器，MCOV额定值15.3kV 在线监测：每台变压器配备一套简化的在线溶解气体分析监测系统，至少监测氢气 温度监测器：Qualitrol ITM 509 型变压器温度监测器，带寿命消耗选项 继电器：包括气体继电器（ABB 12型或等效）、突发压力继电器（Qualitrol 900型）等 抗震等级：LOW（需符合 IEEE 693 Annex U） 需要CSA认证 |  | 3