## 2500
JZPE POWER TRANSFORMER INC. Add: Longxi Industrial Zone ，JiangYan District,Taizhou City, CHINA Email:harper@jiezougroup.com Phone:+86-18896773023(Wechat/Whatsapp)
Technical Data Sheet
NO | SPECIFICATION | UNIT | DATA
General
| Manufacturer |  | CHN
| Model |  | SCB-2000/12.47/0.48
Quantity
Size
| CRT Overall dimension (L x W x H)（Approx.） |  | 1980*1500*2070
| Enclosure dimension (L x W x H)（Approx.） |  | 2600*2100*2700
| Standard |  | IEC 60076-11
Site conditions
| Equipment Location |  | Indoor
| Elevation | m | 585
| Minimum Ambient Temperature | ℃ | -40
| Maximum Ambient Temperature | ℃ | 35
| Hazardous Location |  | Non-Hazardous
| Seismic Zone | PGA | 0.095
Design
| Construction |  | Cast Coil
| Enclosure |  | NEMA 3R
| Rating | kVA | 2000
| Cooling Type |  | AF
System parameters & windings
| Frequency | Hz | 60
| Phase |  | Three phase
Primary
| Connection |  | Delta
| Voltage | V | 12470
| BIL |  | 95
Secondary
| Connection |  | Wye
| Voltage | V | 480/277
| BIL |  | 30
| Vector Configuration |  | Dyn1
| Windings |  | Copper
| Temperature Rise |  | Standard - 100°C above ambient
Impedance and losses
| Standard Impedance |  | Standard Impedance Used
| Percentage | % | 5.95
| Other Impedance |  | Other Impedance Used
| Percentage | %
| No-Load Losses | kW | 3.4
| Load Losses | kW | 15.3
Efficiency
| Load Percentage | % | 25 | 50 | 75 | 100 | 133
| 1.0 PF | % | 99.14 | 99.28 | 99.21 | 99.07 | 98.87
| 0.8 PF | % | 98.92 | 99.2 | 99.12 | 98.97 | 98.8
Tap changer
| Type |  | Off-Load
Primary
| Tap Changer Specifications |  | (2) 2.5% FCAN, (2) 2.5% FCBN
External connections
| Primary Connection |  | Bus bar
| Material |  | Copper
| Size & No. Per |  | 4*40
| Secondary Connection |  | Bus bar
| Material |  | Copper
| Size & No. Per |  | 12*120
Accessories
| Accessories |  | Standard Accessories
Winding Temp. Alarm Contacts
| Other Accessories |  | Jack and Roll Skid Base
Impact recorder
Miscellaneous
Weights
| Total Installed | kg | 3850
| Sound Level |  | 55dBA@2000kVA
Notes:
1 ' * ' Indicates to be completed by the vendor when not provided by the buyer.