3000KVA 33kV OIL IMMERSED TRANSFORMER

DATA SHEET

Basic information

Manufacturer name :                                                 JZPE POWER TRANSFORMER INC.

Product brand:                                                           JIEZOU

Product type:                                                              oil immersed transformer

Standard:                                                                    IEC-60076

Rated capacity:                                                           3000kva

Primary voltage:                                                         33Kv

Tapping range                                                             ±2x2.5%

Secondary voltage(load):                                           0.415Kv

Impedance:                                                                 7.0%

Vector group:                                                              Dyn11

Frequency:                                                                  50hz

Nos. Of phase:                                                            three

Cooling method:                                                         ONAN

Winding material:                                                       Copper

Technical data

Type of installation:                                                    outdoor

Level of insulation:                                                      A

Mounting mode:                                                         Pad mounted

Oil top temperature rise:                                             50℃

Winding temperature rise:                                          55℃

No-load losses:                                                           2880w

Load-losses:                                                               21660w

No-load current:                                                         0.58%

Ambient temperature for operation:                           -10℃ to 50℃

Noise level:                                                                 <52

Short circuit thermal time                                           ≥5s

Insulation levels(HV)(LI/AC/Umax)                          75/30kv

Weight information:

Oil Weight:                                                                 1620kg

Machine weight:                                                         4500kg

Total weight:                                                               8000kg

Dimension information:

Length:                                                                        2700mm

Width:                                                                         3000mm

Height:                                                                        2800mm

Accessories

Off-load tap changer(1pc)                                           YES

Transformer lifting lugs(2pcs)                                     YES

Grounding terminal(2pcs)                                            YES

Nameplate according to IEC60076-1(1pc)                  YES

Thermal meter pocket                                                  YES

Oil level indicator                                                         YES

Pressure Valve                                                              YES