## 1000kva
JZPE POWER TRANSFORMER INC. Add: Longxi Industrial Zone ，JiangYan District,Taizhou City, CHINA Email:harper@jiezougroup.com Phone:+86-18896773023(Wechat/Whatsapp)
Transformer, Three Phase, Pad Mount, 1000kVA , |  |  |  |  | 注意
ITEM | DATA | UNIT | Offered | Comment
1 | Supplier | ….
2 | Model | …. | JZPE-H-1000/13,800GrdY/7970x 480 Y/ 277
3 | Country of origin | …. | CHINA
4 | Standard manufacturing and testing | …. | ANSI/IEEE
5 | Features
5.1 | Type |  | Loop feed pad mount
5.2 | Installation |  | Outdoor
5.3 | Altitude above sea level | m/℃ | 1000
5.5 | Rated Power | kVA | 2000
5.6 | HV | V | 13,800GrdY/7970
5.7 | LV | V | 480 Y/ 277
5.8 | Rated Frequency | Hz | 60
5.9 | Cooling System |  | ONAN
6 | Number of winding |  | 2
6.1 | Number of phase |  | 3
6.2 | Core/Shell |  | Core type
6.3 | Refrigerant |  | Mineral oil (No PCB)
6.4 | Working-Temperature | °C | -50°C to +40°C
6.6 | The temperature rise -Top oil | °C | 65
6.7 | The temperature rise --Winding | °C | 65
6.8 | Hot spot | °C | 80
7.1 | Losses
7.1.1 | No load losses at rated voltage and rated frequency on principal tap | W | 1500
7.1.2 | Load loss at rated voltage | W | 11200
7.1.3 | Tolerance |  | 10% NLL, 6% Total Loss
7.2 | Vector Group |  | YNyn0
7.3 | Core material |  | Grain oriented silicon steel
7.4 | Core legged |  | 3
7.5 | Winding material |  | Aluminum
7.6 | Tap changer
7.6.1 | On load or off-circuit |  | off-circuit
7.6.2 | Position of tapped winding
7.6.3 | Tap Voltages HV | % | ±2x2.5%
7.7 | High voltage electrical characteristics of transformers and assembled load break terminals
7.7.1 | Insulation class | kv | 15
7.7.2 | BIL | kV | 95
7.8 | Low voltage
7.8.1 | Insulation class | kV | 1.2
7.8.2 | BIL | kV | 30
7.8.3 | Audible sound level | db | 55
7.9 | Short-circuit capability
7.9.1 | withstand capability per unit of base current (symmetrical) |  | 25
7.9.2 | Duration in cycles |  | 120 | 316SS
8 | Impedance | % | 5.75% | Tank: 304L SS
8.0.1 | Impedance tolerance |  | ±7.5% | 304L 316SS
8.1 | Tank |  | Mild steel 低碳钢 | SS Stainless steel
8.1.1 | Colors |  | Munsell Green 7GY3.29/1.5
8.2 | Total Dimentions
8.2.1 | Length | INCH | 1730
8.2.2 | Width | INCH | 1265
8.2.3 | Height | INCH | 1920
8.3 | Weight
8.3.1 | Oil | GAL | 370
8.3.2 | Total | L | 6450
8.4 | Accessories including:
8.4.1 | HV and LV box |  | 1 | Specific configurations are subject to order design
8.4.2 | Handhole cover |  | 1
8.4.3 | Mineral oil |  | 1
8.4.4 | Tank |  | 1
8.4.5 | Backup Fuse |  | 6
8.4.6 | Jacking Facilities |  | 2
8.4.7 | LV bushing |  | 4
8.4.8 | Oil level gauge |  | 1
8.4.9 | Gas gauge |  | 1
8.5.0 | Oil temperature Gauge |  | 1
8.5.1 | Pressure Relief Value |  | 1
8.5.2 | Oil-in Plug |  | 1
8.5.3 | Nameplate |  | 1
8.5.4 | No load Tap changer |  | 1
8.5.5 | Bayonet fuse |  | 3
8.5.6 | Hv bushing |  | 3
9 | Warranty: | Years | 2