## Sheet1
JZPE POWER TRANSFORMER INC. Add: Longxi Industrial Zone ，JiangYan District,Taizhou City, CHINA Email:harper@jiezougroup.com Phone:+86-18896773023(Wechat/Whatsapp)
POWER TRANSFORMER 69/22.8 kV- 10/12.5MVA TECHNICAL DATA SCHEDULE
Description | Units | Guaranteed Value
Manufacturer
Country of origin
Model |  | SFZ-12500/69
Arrangement |  | outdoor
Standards |  | ANSI C57.12.00
Single- or three-phase unit |  | three-phase
Type |  | core type
Type of tank |  | upper flange type
Number of phase |  | 3
Number of windings |  | 2
kinematic viscosity at 40 °C | mm²/s | Max. 10.0
dielectric dissipation factor at 90℃ (after pre-treatment) | mm²/s | Max. 0.002
Ratings
Rated power | kVA | 10000/12500
Ambient temperature
-Absolute maximum | °C | 45
-Annual average | °C | 25
Maximum service altitude | m | 2000
Temperature rise
-oil / top | oC | 55
-windings / average | oC | 65
-windings hot spot | oC | 75
Rated voltages:
-primary | kV | 69
-secondary | kV | 22.8
Rated frequency | Hz | 60
Permissible load of neutral point | % | 100
Vector group symbol |  | Dyn1
Impedance voltage at 10MVA | % | 7.38
Magnetic flux density | Tesla | 1.70 (Max)
Over-and under-excitation within specified temperature rise limit | % | 10
No-load losses | kW | 15
No-load current | A | 0.2
Maximum permissible Core losses | W/kg | 1.2 (Max)
Current density (at all tap changer settings and in all parts of the windings) | A/mm² | 3 (Max)
Guaranteed Load losses at 10MVA | kW | 47.8
Tapping range at primary side (69kV) | % | ±2×2.5
Number of steps | steps | 5
Insulation Level / Primary winding
- Lightning impulse level (lines / neutral) | kV | 350
- Power frequency withstand voltage (lines / neutral) | kV | 140
Insulation Level / Secondary winding
-Lightning impulse level (lines / neutral) | kV | 150
-Power frequency withstand voltage (lines / neutral) | kV | 50
Cooling method |  | ONAN/ONAF
Bushings Primary (lines and neutral)
Manufacturer |  | CHN
Type |  | Oil impregnated paper
Kind of condenser bushing
Power frequency test voltage | kV | 140
Lightning impulse level | kV | 350
Minimum creepage distance | mm/kV | 31
Bushing Secondary (lines and neutral)
manufacturer |  | CHN
type |  | Oil filled porcelain
kind of bushing
power frequency test voltage | kV | 85
lightning impulse level | kV | 200
minimum creepage distance | mm/kV | 31
N0-Load Tap Changer (Mounted on the Primary High Voltage winding)
Manufacturer |  | CHN
Type |  | WDTII
Rated through current | A | 200
Lightning impulse level (1.2 / 50 µs) | kV | 350
Power frequency withstand test voltage (r.m.s. value) | kV | 140
Transformer masses:
Active part | kg | 10610
Insulation liquid | kg | 5690
Accessories | kg | 830
Transportation | kg | 17720
Total | kg | 23400
Overall dimensions including bushings:
Length | mm | 4910
Width | mm | 3800
Height | mm | 4000
Shipping dimensions:
Length | mm | 3910
Width | mm | 1700
Height | mm | 2600
Height of crane hooks | mm | 5000